## Complete
Annex D.1 eq# | (D.1) | (D.2) | (D.3) | (D.4) | (D.5) | (D.6) | (D.7) |  | (D.9) | (D.11) | (D.13) | (D.14) | (D.15) | (D.16) | (D.17) | (D.18) | [7 empty] | (D.19) | (D.20) | (D.21) |  |  | (D.22) |  | (D.24) | (D.26) | (D.28) | (D.29) | (D.30) | (D.31) | (D.32) |  | (D.34) | (D.36) | (D.38) | (D.39) | (D.40) | (D.41) | (D.42) | (D.43) | (D.44) | (D.45) | (D.46) | (D.47) | (D.48) | (D.49) | (D.50) | (D.51) | (D.52) |  | (D.54) | (D.56) | (D.58) | (D.59) | (D.60) | (D.61) | (D.62) |  | (D.64) | (D.66) | (D.68) | (D.69) | (D.70) | (D.71) | (D.72)
Annex D.2 eq# | (D.73) | (D.74) | (D.75) | (D.76) | (D.77) | (D.78) | (D.79) | (D.80) | (D.82) | [5 empty] | (D.84) | (D.85) | [7 empty] | (D.86) | (D.87) | (D.88) |  |  | (D.89) | (D.91) | [6 empty] | (D.92) | (D.94) | [6 empty] | (D.95) | (D.96) | (D.97) | [6 empty] | (D.99) | (D.100) | (D.102) | [6 empty] | (D.103) | (D.105) | [6 empty] | (D.106)
Input parameters | (D.82): Arcing Current | [6 empty] | Tarc | Enclosure Size Correction Factor | [12 empty] | Incident Energy | [7 empty] | Arc-Flash Boundary | [7 empty] | Correction Factor |  | Arcing Current (Reduced) | [6 empty] | Tarc | Incident Energy (Reduced) | [7 empty] | Arc-Flash Boundary (Reduced)
| (D.82): Intermediate |  |  | Final | [17 empty] | Intermediate |  |  |  | Final |  |  |  | Intermediate |  |  |  | Final | [5 empty] | Intermediate |  |  | Final |  |  |  |  | Intermediate |  |  |  | Final |  |  |  | Intermediate |  |  |  | Final
Bus Name | Config | Voc | Ibf | Gap | WDist | Width | Height | Depth | Iarc_600 | Iarc_2700 | Iarc_14300 | Iarc_1 | Iarc_2 | Iarc_3 | Iarc | T | Type | A | B | Width11 | Eq_11 | Height12 | Eq_12 | Width1 | Height1 | ESS | Eq_14 | Eq_15 | CF | E≤600 | E600 | E2700 | E14300 | E1 | E2 | E3 | E | AFB≤600 | AFB600 | AFB2700 | AFB14300 | AFB1 | AFB2 | AFB3 | AFB | VarCf | 1-0,5*VarCf | Iarc_600_min | Iarc_2700_min | Iarc_14300_min | Iarc_1 | Iarc_2 | Iarc_3 | Iarc_min | T | E≤600 | E600 | E2700 | E14300 | E1 | E2 | E3 | E | AFB≤600 | AFB600 | AFB2700 | AFB14300 | AFB1 | AFB2 | AFB3 | AFB
|  | [kV] | [kA] | [mm] | [mm] | [mm] | [mm] | [mm] | [kA] | [kA] | [kA] | [kA] | [kA] | [kA] | [kA] | [ms] | [13 empty] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] |  |  | [kA] | [kA] | [kA] | [kA] | [kA] | [kA] | [kA] | [ms] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [J/cm²] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm]
Annex D.1 | VCB | 4.16 | 15 | 104 | 914.4 | 762 | 1143 | 254 | 11.1167 | 12.8158 | 14.1165 | 13.997 | 12.9795 | 12.272 | 12.9795 | 197 | Typical | 4 | 20 | 762 | 27.632 | 1143 | 33.752 | 27.632 | 44.9999 | 36.316 | 1.2838 | 0.38103 | 1.2838 | 10.0351 | 8.6524 | 11.9768 | 13.3668 | 14.288 | 12.1517 | 10.6665 | 12.1517 | 1410.3948 | 1285.4283 | 1591.3956 | 1707.4373 | 1804.1157 | 1606.0008 | 1468.2638 | 1606.0008 | 0.046872 | 0.97656 | 10.8562 | 12.5154 | 13.7856 | 13.669 | 12.6753 | 11.9844 | 12.6753 | 223 | 11.1047 | 8.9803 | 13.0182 | 15.6016 | 15.8255 | 13.3433 | 11.6177 | 13.3433 | 1502.6713 | 1315.7034 | 1678.2497 | 1884.3588 | 1930.3058 | 1704.1911 | 1546.9875 | 1704.1911
Annex D.2 | VCB | 0.48 | 45 | 32 | 609.6 | 610 | 610 | 254 | 32.4487 | 38.643 | 42.5674 | 32.0947 | 37.8919 | 31.7634 | 28.7933 | 61.3 | Typical | 4 | 20 | 610 | 25.5555 | 610 | 25.5555 | 24.0157 | 24.0157 | 24.0157 | 1.0847 | 0.77525 | 1.0847 | 11.585 | 12.9888 | 20.6378 | 22.7313 | 12.5517 | 20.2372 | 12.1125 | 11.585 | 1028.679 | 1105.0068 | 1500.7478 | 1597.0458 | 1082.393 | 1482.3183 | 1059.5401 | 1028.679 | 0.24651 | 0.87675 | 28.4493 | 33.8801 | 37.3208 | 28.1389 | 33.2216 | 27.8485 | 25.2444 | 319 | 53.1563 | 40.5061 | 85.9415 | 139.2098 | 37.9097 | 75.7471 | 35.7476 | 53.1563 | 2668.9188 | 2251.4956 | 3725.3742 | 5072.941 | 2167.274 | 3467.4778 | 2092.9767 | 2668.9188
PN-01A | VCBB | 13.8 | 17.563 | 153 | 914.4 | 800 | 1135 | 900 | 13.9962 | 15.4726 | 16.8151 | 23.2763 | 16.7572 | -17.7011 | 16.7572 | 180 | Typical | 10 | 24 | 800 | 31.4503 | 1135 | 44.5293 | 31.4503 | 44.5293 | 37.9898 | 1.2652 | 4.0176 | 1.2652 | 13.982 | 11.2855 | 19.038 | 25.5515 | 60.0152 | 25.2707 | -158.3786 | 25.2707 | 1610.7029 | 1430.8045 | 1965.2851 | 2412.735 | 4790.3968 | 2393.4484 | -10276.1359 | 2393.4484 | 0.037875 | 0.98106 | 13.7312 | 15.1796 | 16.4966 | 22.8355 | 16.4399 | -17.3659 | 16.4399 | 180 | 13.6674 | 11.065 | 19.2118 | 25.6946 | 62.2733 | 25.4152 | -169.4063 | 25.4152 | 1590.5718 | 1415.2808 | 1975.5646 | 2420.786 | 4937.0645 | 2401.5954 | -11000.1697 | 2401.5954
PN-01B | VCBB | 13.8 | 19.776 | 153 | 914.4 | 800 | 1135 | 900 | 15.7738 | 17.3769 | 18.9183 | 25.8507 | 18.8518 | -18.1424 | 18.8518 | 180 | Typical | 10 | 24 | 800 | 31.4503 | 1135 | 44.5293 | 31.4503 | 44.5293 | 37.9898 | 1.2652 | 4.0176 | 1.2652 | 15.9776 | 12.9236 | 21.6259 | 28.9045 | 67.6236 | 28.5908 | -177.726 | 28.5908 | 1733.9846 | 1542.1212 | 2114.468 | 2596.8156 | 5139.7298 | 2576.0248 | -10974.9878 | 2576.0248 | 0.037875 | 0.98106 | 15.4751 | 17.0479 | 18.56 | 25.3612 | 18.4948 | -17.7988 | 18.4948 | 180 | 15.6181 | 12.671 | 21.8229 | 29.0673 | 70.1975 | 28.755 | -190.298 | 28.755 | 1712.3127 | 1525.3837 | 2125.5062 | 2605.5285 | 5297.5818 | 2584.8379 | -11753.9517 | 2584.8379
PN-02A | VCBB | 4.16 | 10.95 | 102 | 914.4 | 400 | 750 | 500 | 8.7963 | 9.8016 | 10.5661 | 10.5006 | 9.8979 | 9.4788 | 9.8979 | 380 | Typical | 10 | 24 | 400 | 19.9513 | 750 | 28.0813 | 20 | 28.0813 | 24.0406 | 1.0763 | 1.0131 | 1.0763 | 17.0855 | 14.8474 | 26.3355 | 35.5459 | 34.3225 | 27.4947 | 22.7478 | 27.4947 | 1799.4555 | 1665.0722 | 2367.6721 | 2937.6719 | 2856.1464 | 2439.4135 | 2149.6849 | 2439.4135 | 0.043272 | 0.97836 | 8.606 | 9.5896 | 10.3375 | 10.2734 | 9.6837 | 9.2737 | 9.6837 | 380 | 16.6465 | 14.5174 | 26.6163 | 35.7716 | 35.0279 | 27.7686 | 22.7216 | 27.7686 | 1773.7486 | 1644.5107 | 2382.1303 | 2948.7833 | 2894.9515 | 2453.4504 | 2146.502 | 2453.4504
PN-02B | VCBB | 4.16 | 10.95 | 102 | 914.4 | 400 | 750 | 500 | 8.7963 | 9.8016 | 10.5661 | 10.5006 | 9.8979 | 9.4788 | 9.8979 | 380 | Typical | 10 | 24 | 400 | 19.9513 | 750 | 28.0813 | 20 | 28.0813 | 24.0406 | 1.0763 | 1.0131 | 1.0763 | 17.0855 | 14.8474 | 26.3355 | 35.5459 | 34.3225 | 27.4947 | 22.7478 | 27.4947 | 1799.4555 | 1665.0722 | 2367.6721 | 2937.6719 | 2856.1464 | 2439.4135 | 2149.6849 | 2439.4135 | 0.043272 | 0.97836 | 8.606 | 9.5896 | 10.3375 | 10.2734 | 9.6837 | 9.2737 | 9.6837 | 380 | 16.6465 | 14.5174 | 26.6163 | 35.7716 | 35.0279 | 27.7686 | 22.7216 | 27.7686 | 1773.7486 | 1644.5107 | 2382.1303 | 2948.7833 | 2894.9515 | 2453.4504 | 2146.502 | 2453.4504
PN-03A | VCBB | 0.48 | 32.158 | 32 | 609.6 | 800 | 750 | 500 | 27.1652 | 28.4945 | 31.127 | 27.0892 | 27.9907 | 27.0377 | 25.2102 | 350 | Typical | 10 | 24 | 800 | 28.3999 | 750 | 27.5404 | 28.3999 | 27.5404 | 27.9702 | 1.1412 | 1.1255 | 1.1412 | 64.8027 | 70.8259 | 117.9922 | 144.7688 | 68.1306 | 112.8676 | 65.5742 | 64.8027 | 2506.6683 | 2632.8984 | 3733.5107 | 4524.6905 | 2570.0063 | 3582.0953 | 2512.1726 | 2506.6683 | 0.23675 | 0.88163 | 23.9495 | 25.1215 | 27.4424 | 23.8826 | 24.6774 | 23.8371 | 22.226 | 350 | 55.7804 | 62.2061 | 124.3974 | 149.4162 | 58.6523 | 119.6093 | 55.169 | 55.7804 | 2307.2985 | 2450.6382 | 3848.5455 | 4610.752 | 2370.7578 | 3702.6749 | 2294.6482 | 2307.2985
PN-03B | VCBB | 0.48 | 32.158 | 32 | 609.6 | 800 | 750 | 500 | 27.1652 | 28.4945 | 31.127 | 27.0892 | 27.9907 | 27.0377 | 25.2102 | 350 | Typical | 10 | 24 | 800 | 28.3999 | 750 | 27.5404 | 28.3999 | 27.5404 | 27.9702 | 1.1412 | 1.1255 | 1.1412 | 64.8027 | 70.8259 | 117.9922 | 144.7688 | 68.1306 | 112.8676 | 65.5742 | 64.8027 | 2506.6683 | 2632.8984 | 3733.5107 | 4524.6905 | 2570.0063 | 3582.0953 | 2512.1726 | 2506.6683 | 0.23675 | 0.88163 | 23.9495 | 25.1215 | 27.4424 | 23.8826 | 24.6774 | 23.8371 | 22.226 | 350 | 55.7804 | 62.2061 | 124.3974 | 149.4162 | 58.6523 | 119.6093 | 55.169 | 55.7804 | 2307.2985 | 2450.6382 | 3848.5455 | 4610.752 | 2370.7578 | 3702.6749 | 2294.6482 | 2307.2985
PN-04A | VCBB | 0.48 | 30.253 | 25 | 457.2 | 437 | 215 | 460 | 26.0228 | 26.9333 | 29.3765 | 25.9707 | 26.4657 | 25.9424 | 24.3054 | 125 | Typical | 10 | 24 | 437 | 22.1594 | 215 | 18.3429 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 39.9626 | 43.345 | 70.9328 | 85.0362 | 41.7685 | 68.2338 | 40.2562 | 39.9626 | 1439.1487 | 1505.2572 | 2090.7865 | 2470.9372 | 1471.7984 | 2018.0336 | 1440.5849 | 1439.1487 | 0.23675 | 0.88163 | 22.9423 | 23.7451 | 25.899 | 22.8965 | 23.3328 | 22.8715 | 21.4283 | 125 | 34.3987 | 38.0802 | 74.8318 | 87.793 | 35.9801 | 72.3513 | 33.9017 | 34.3987 | 1324.6849 | 1401.2702 | 2156.0061 | 2518.3966 | 1358.1424 | 2086.652 | 1316.5133 | 1324.6849
PN-04B | VCBB | 0.48 | 28.596 | 25 | 457.2 | 437 | 215 | 460 | 24.7038 | 25.4937 | 27.7828 | 24.6586 | 25.0556 | 24.636 | 23.1098 | 125 | Typical | 10 | 24 | 437 | 22.1594 | 215 | 18.3429 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 37.7546 | 40.8733 | 66.7801 | 80.2176 | 39.3929 | 64.2085 | 37.9749 | 37.7546 | 1394.6345 | 1457.1873 | 2019.6189 | 2386.4631 | 1425.0483 | 1949.4125 | 1395.0847 | 1394.6345 | 0.23675 | 0.88163 | 21.7795 | 22.4759 | 24.4941 | 21.7397 | 22.0897 | 21.7197 | 20.3742 | 125 | 32.4981 | 35.9096 | 70.4546 | 82.8104 | 33.9356 | 68.0899 | 31.9839 | 32.4981 | 1283.7112 | 1356.5384 | 2082.6827 | 2432.1649 | 1315.0444 | 2015.799 | 1275.0013 | 1283.7112
PN-04C | VCBB | 0.48 | 30.253 | 25 | 457.2 | 437 | 215 | 460 | 26.0228 | 26.9333 | 29.3765 | 25.9707 | 26.4657 | 25.9424 | 24.3054 | 125 | Typical | 10 | 24 | 437 | 22.1594 | 215 | 18.3429 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 39.9626 | 43.345 | 70.9328 | 85.0362 | 41.7685 | 68.2338 | 40.2562 | 39.9626 | 1439.1487 | 1505.2572 | 2090.7865 | 2470.9372 | 1471.7984 | 2018.0336 | 1440.5849 | 1439.1487 | 0.23675 | 0.88163 | 22.9423 | 23.7451 | 25.899 | 22.8965 | 23.3328 | 22.8715 | 21.4283 | 125 | 34.3987 | 38.0802 | 74.8318 | 87.793 | 35.9801 | 72.3513 | 33.9017 | 34.3987 | 1324.6849 | 1401.2702 | 2156.0061 | 2518.3966 | 1358.1424 | 2086.652 | 1316.5133 | 1324.6849
PN-05 | VCBB | 0.48 | 29.939 | 25 | 457.2 | 420 | 290 | 450 | 25.775 | 26.6608 | 29.0747 | 25.7244 | 26.1988 | 25.6973 | 24.0816 | 125 | Typical | 10 | 24 | 420 | 21.8671 | 290 | 19.6322 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 39.5485 | 42.8797 | 70.1452 | 84.1229 | 41.3216 | 67.4701 | 39.8274 | 39.5485 | 1430.8851 | 1496.3034 | 2077.4267 | 2455.0785 | 1463.0964 | 2005.1519 | 1432.1218 | 1430.8851 | 0.23675 | 0.88163 | 22.7239 | 23.5049 | 25.633 | 22.6793 | 23.0976 | 22.6554 | 21.231 | 125 | 34.0423 | 37.6716 | 74.0015 | 86.8486 | 35.5956 | 71.5429 | 33.5414 | 34.0423 | 1317.0786 | 1392.9383 | 2142.2417 | 2502.2076 | 1350.1209 | 2073.3517 | 1308.7935 | 1317.0786
PN-06A | VCBB | 0.48 | 30.377 | 25 | 457.2 | 420 | 290 | 450 | 26.1203 | 27.0408 | 29.4956 | 26.0677 | 26.571 | 26.0389 | 24.3934 | 125 | Typical | 10 | 24 | 420 | 21.8671 | 290 | 19.6322 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 40.1256 | 43.5283 | 71.244 | 85.3969 | 41.9445 | 68.5354 | 40.425 | 40.1256 | 1442.39 | 1508.7733 | 2096.0464 | 2477.181 | 1475.2148 | 2023.1052 | 1443.9068 | 1442.39 | 0.23675 | 0.88163 | 23.0283 | 23.8399 | 26.0041 | 22.982 | 23.4257 | 22.9566 | 21.5058 | 125 | 34.539 | 38.2412 | 75.1598 | 88.166 | 36.1315 | 72.6706 | 34.0436 | 34.539 | 1327.6685 | 1404.5421 | 2161.4252 | 2524.7706 | 1361.2916 | 2091.8884 | 1319.5432 | 1327.6685
PN-06B | VCBB | 0.48 | 30.377 | 25 | 457.2 | 420 | 290 | 450 | 26.1203 | 27.0408 | 29.4956 | 26.0677 | 26.571 | 26.0389 | 24.3934 | 125 | Typical | 10 | 24 | 420 | 21.8671 | 290 | 19.6322 | 20 | 20 | 20 | 0.99996 | 1.001 | 0.99996 | 40.1256 | 43.5283 | 71.244 | 85.3969 | 41.9445 | 68.5354 | 40.425 | 40.1256 | 1442.39 | 1508.7733 | 2096.0464 | 2477.181 | 1475.2148 | 2023.1052 | 1443.9068 | 1442.39 | 0.23675 | 0.88163 | 23.0283 | 23.8399 | 26.0041 | 22.982 | 23.4257 | 22.9566 | 21.5058 | 125 | 34.539 | 38.2412 | 75.1598 | 88.166 | 36.1315 | 72.6706 | 34.0436 | 34.539 | 1327.6685 | 1404.5421 | 2161.4252 | 2524.7706 | 1361.2916 | 2091.8884 | 1319.5432 | 1327.6685
PN-07 | VCBB | 0.48 | 13.616 | 25 | 457.2 | 600 | 1200 | 250 | 11.8138 | 12.3413 | 13.3006 | 11.7836 | 12.1577 | 11.7622 | 11.0692 | 20 | Typical | 10 | 24 | 600 | 24.9616 | 1200 | 35.2766 | 23.622 | 35.2766 | 29.4493 | 1.1633 | 1.206 | 1.1633 | 2.2552 | 2.4368 | 4.1403 | 5.1059 | 2.3395 | 3.9555 | 2.2471 | 2.2552 | 293.7385 | 306.5905 | 409.2945 | 461.8058 | 300.7217 | 399.2449 | 295.0918 | 293.7385 | 0.23675 | 0.88163 | 10.4153 | 10.8804 | 11.7262 | 10.3887 | 10.7186 | 10.3699 | 9.7589 | 20 | 1.9412 | 2.1416 | 4.3712 | 5.2645 | 2.0141 | 4.2003 | 1.8892 | 1.9412 | 270.3758 | 285.4623 | 422.2469 | 470.3066 | 277.646 | 413.0493 | 269.9087 | 270.3758

## Table1
E.C. | Voc | k1 | k2 | k3 | k4 | k5 | k6 | k7 | k8 | k9 | k10
VCB | 600 | -0.04287 | 1.035 | -0.083 | 0 | 0 | -4.783e-09 | 1.962e-06 | -0.000229 | 0.003141 | 1.092
VCB | 2700 | 0.0065 | 1.001 | -0.024 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729
VCB | 14300 | 0.005795 | 1.015 | -0.011 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729
VCBB | 600 | -0.017432 | 0.98 | -0.05 | 0 | 0 | -5.767e-09 | 2.524e-06 | -0.00034 | 0.01187 | 1.013
VCBB | 2700 | 0.002823 | 0.995 | -0.0125 | 0 | -9.204e-11 | 2.901e-08 | -3.262e-06 | 0.0001569 | -0.004003 | 0.9825
VCBB | 14300 | 0.014827 | 1.01 | -0.01 | 0 | -9.204e-11 | 2.901e-08 | -3.262e-06 | 0.0001569 | -0.004003 | 0.9825
HCB | 600 | 0.054922 | 0.988 | -0.11 | 0 | 0 | -5.382e-09 | 2.316e-06 | -0.000302 | 0.0091 | 0.9725
HCB | 2700 | 0.001011 | 1.003 | -0.0249 | 0 | 0 | 4.859e-10 | -1.814e-07 | -9.128e-06 | -0.0007 | 0.9881
HCB | 14300 | 0.008693 | 0.999 | -0.02 | 0 | -5.043e-11 | 2.233e-08 | -3.046e-06 | 0.000116 | -0.001145 | 0.9839
VOA | 600 | 0.043785 | 1.04 | -0.18 | 0 | 0 | -4.783e-09 | 1.962e-06 | -0.000229 | 0.003141 | 1.092
VOA | 2700 | -0.02395 | 1.006 | -0.0188 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729
VOA | 14300 | 0.005371 | 1.0102 | -0.029 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729
HOA | 600 | 0.11115 | 1.008 | -0.24 | 0 | 0 | -3.895e-09 | 1.641e-06 | -0.000197 | 0.002615 | 1.1
HOA | 2700 | 0.000435 | 1.006 | -0.038 | 0 | 0 | 7.859e-10 | -1.914e-07 | -9.128e-06 | -0.0007 | 0.9981
HOA | 14300 | 0.000904 | 0.999 | -0.02 | 0 | 0 | 7.859e-10 | -1.914e-07 | -9.128e-06 | -0.0007 | 0.9981

## Table2
E.C. | k1 | k2 | k3 | k4 | k5 | k6 | k7
VCB | 0 | -1.4269e-06 | 8.3137e-05 | -0.0019382 | 0.022366 | -0.12645 | 0.30226
VCBB | 1.138e-06 | -6.0287e-05 | 0.0012758 | -0.013778 | 0.080217 | -0.24066 | 0.33524
HCB | 0 | -3.097e-06 | 0.00016405 | -0.0033609 | 0.033308 | -0.16182 | 0.34627
VOA | 9.5606e-07 | -5.1543e-05 | 0.0011161 | -0.01242 | 0.075125 | -0.23584 | 0.33696
HOA | 0 | -3.1555e-06 | 0.0001682 | -0.0034607 | 0.034124 | -0.1599 | 0.34629

## Table3
600 | k1 | k2 | k3 | k4 | k5 | k6 | k7 | k8 | k9 | k10 | k11 | k12 | k13
VCB | 0.75336 | 0.566 | 1.7526 | 0 | 0 | -4.783e-09 | 1.962e-06 | -0.000229 | 0.003141 | 1.092 | 0 | -1.598 | 0.957
VCBB | 3.0685 | 0.26 | -0.098107 | 0 | 0 | -5.767e-09 | 2.524e-06 | -0.00034 | 0.01187 | 1.013 | -0.06 | -1.809 | 1.19
HCB | 4.0737 | 0.344 | -0.37026 | 0 | 0 | -5.382e-09 | 2.316e-06 | -0.000302 | 0.0091 | 0.9725 | 0 | -2.03 | 1.036
VOA | 0.67929 | 0.746 | 1.2226 | 0 | 0 | -4.783e-09 | 1.962e-06 | -0.000229 | 0.003141 | 1.092 | 0 | -1.598 | 0.997
HOA | 3.4704 | 0.465 | -0.26186 | 0 | 0 | -3.895e-09 | 1.641e-06 | -0.000197 | 0.002615 | 1.1 | 0 | -1.99 | 1.04

## Table4
2700 | k1 | k2 | k3 | k4 | k5 | k6 | k7 | k8 | k9 | k10 | k11 | k12 | k13
VCB | 2.4002 | 0.165 | 0.3542 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729 | 0 | -1.569 | 0.9778
VCBB | 3.8706 | 0.185 | -0.73662 | 0 | -9.204e-11 | 2.901e-08 | -3.262e-06 | 0.0001569 | -0.004003 | 0.9825 | 0 | -1.742 | 1.09
HCB | 3.4864 | 0.177 | -0.1931 | 0 | 0 | 4.859e-10 | -1.814e-07 | -9.128e-06 | -0.0007 | 0.9881 | 0.027 | -1.723 | 1.055
VOA | 3.8807 | 0.105 | -1.906 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729 | 0 | -1.515 | 1.115
HOA | 3.6163 | 0.149 | -0.76156 | 0 | 0 | 7.859e-10 | -1.914e-07 | -9.128e-06 | -0.0007 | 0.9981 | 0 | -1.639 | 1.078

## Table5
14300 | k1 | k2 | k3 | k4 | k5 | k6 | k7 | k8 | k9 | k10 | k11 | k12 | k13
VCB | 3.8259 | 0.11 | -0.99975 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729 | 0 | -1.568 | 0.99
VCBB | 3.6443 | 0.215 | -0.58552 | 0 | -9.204e-11 | 2.901e-08 | -3.262e-06 | 0.0001569 | -0.004003 | 0.9825 | 0 | -1.677 | 1.06
HCB | 3.0445 | 0.125 | 0.24511 | 0 | -5.043e-11 | 2.233e-08 | -3.046e-06 | 0.000116 | -0.001145 | 0.9839 | 0 | -1.655 | 1.084
VOA | 3.4055 | 0.12 | -0.93245 | -1.557e-12 | 4.556e-10 | -4.186e-08 | 8.346e-07 | 5.482e-05 | -0.003191 | 0.9729 | 0 | -1.534 | 0.979
HOA | 2.0405 | 0.177 | 1.0051 | 0 | 0 | 7.859e-10 | -1.914e-07 | -9.128e-06 | -0.0007 | 0.9981 | -0.05 | -1.633 | 1.151

## Table7
Box type | E.C. | b1 | b2 | b3
Typical | VCB | -0.000302 | 0.03441 | 0.4325
Typical | VCBB | -0.0002976 | 0.032 | 0.479
Typical | HCB | -0.0001923 | 0.01935 | 0.6899
Shallow | VCB | 0.002222 | -0.02556 | 0.6222
Shallow | VCBB | -0.002778 | 0.1194 | -0.2778
Shallow | HCB | -0.0005556 | 0.03722 | 0.4778